## TS
NAME OF PROJECT :- 220kV/110kV M/C MV KOTTAYAM - THURAVOOR TRANSMISSION LINE (PART-2)
NAME OF CLIENT :- KERALA STATE ELECTRICITY BOARD
NAME OF AGENCY :- FOR SOLUTIONS
DETAILED SURVEY TOWER SCHEDULE (LINE LENGTH: 4.393 Km)
Sl No | Loc No. | Tower Type | Deviation Angle (DMS) | Span (m) | Section Length (m) | Cum. Chainage (m) | Wind Span (m) | Adjacent Span |  |  | Weight Span (Cold) |  |  | Weight Span (Hot) |  |  | Major Crossings/Remarks | UTM Coordinate (Zone - 43P) |  |  | Twr Extn | Chimney Ht | Spherical Coordinate |  | Existing Tower No. | Weight Span Check | Land Use | Soil Clasification
[8 empty] | Left | Right | Total | Left | Right | Total | Left | Right | Total |  | Easting | Northing | Elevation |  |  | Longitude | Latitude
0 | 72 | KLB+09 | 00°03'00" RT |  | 0 | 0 | 309.35 | 298.7 | 320 | 618.7 | 238.8 | 159.754 | 398.554 | 210 | 159.8334 | 369.8334 |  | 650665.609 | 1080588.581 | 2.151 | 9 |  |  |  |  | Ok
|  |  |  | 320 | [12 empty] | Kayal
1 | 72A | KLA+09 |  |  |  | 320 | 135.4 | 320 | 270.8 | 590.8 | 160.246 | 134.5481 | 294.794 | 160.1666 | 134.823 | 294.9896 |  | 650347.912 | 1080550.28 | 2.18 | 9
270.8
2 | 73 | KLB+09 | 00°01'21" LT |  | 590.8 | 590.8 | 292.35 | 270.8 | 264.7 | 535.5 | 136.2519 | 216.8298 | 353.0817 | 135.977 | 189.5628 | 325.5398 |  | 650079.108 | 1080517.874 | 2.265 | 9 |  |  |  |  | Ok
|  |  |  | 264.7 | [12 empty] | Building 4nos, Road, LT Line
3 | 74 | KLD+00 | 06°46'37" RT |  | 264.7 | 855.5 | 281.5 | 264.7 | 298.3 | 563 | 47.8702 | 93.0111 | 140.8813 | 75.1372 | 111.1307 | 186.2679 |  | 649816.316 | 1080486.088 | 3.026 | 0 |  |  |  |  | Ok
|  |  |  | 298.3 | [12 empty] | Building 4nos, Well
4 | 75 | KLA+06 | 00°29'29" LT |  | 298.3 | 1153.8 | 311.8 | 298.3 | 325.3 | 623.6 | 205.2889 | 162.3496 | 367.6386 | 187.1693 | 162.4466 | 349.6159 |  | 649518.042 | 1080485.464 | 3.196 | 6 |  |  |  |  | Ok
|  |  |  | 325.3 | [12 empty] | Road 2nos, LT Line 3nos, 11kV Line, Building 3nos, Pond
5 | 76 | KLA+03 | 00°02'19" RT |  | 325.3 | 1479.1 | 350.5 | 325.3 | 375.7 | 701 | 162.9504 | 187.7127 | 350.6631 | 162.8534 | 187.757 | 350.6105 |  | 649192.768 | 1080481.995 | 6.232 | 3 |  |  |  |  | Ok
|  |  |  | 375.7 | [12 empty] | Road, LT Line
6 | 77 | KLB+03 |  |  |  | 1854.8 | 389.8 | 375.7 | 403.9 | 779.6 | 187.9873 | 217.4526 | 405.4399 | 187.943 | 212.449 | 400.3919 |  | 648817.109 | 1080478.241 | 6.251 | 3 |  |  |  |  | Ok
|  |  |  | 403.9 | [12 empty] | Building 4nos
7 | 78 | KLD+00 | 27°37'02" RT |  | 779.6 | 2258.7 | 293.6 | 403.9 | 183.3 | 587.2 | 186.4474 | 113.4756 | 299.923 | 191.451 | 106.4311 | 297.8822 |  | 648413.204 | 1080474.205 | 6.944 | 0 |  |  |  |  | Ok
|  |  |  | 183.3 | [12 empty] | 11kV Line, Road
8 | PU58A | KLD+03 | 57°50'27" RT |  | 183.3 | 2442 | 219.45 | 183.3 | 255.6 | 438.9 | 69.8244 | 91.1018 | 160.9261 | 76.8689 | 102.9466 | 179.8155 |  | 648249.973 | 1080557.536 | 2.47 | 3 |  |  |  |  | Ok
|  |  |  | 255.6 | [12 empty] | Road, 11kV Line, LT Line, Building
9 | PU57 | KLC+06 | 18°18'43" LT |  | 255.6 | 2697.6 | 309.4 | 255.6 | 363.2 | 618.8 | 164.4982 | 188.8262 | 353.3245 | 152.6534 | 186.4939 | 339.1473 |  | 648227.189 | 1080812.096 | 2.926 | 6 |  |  |  |  | Ok
|  |  |  | 363.2 | [12 empty] | Building, LT Line, Paddy Field
10 | PU55 | KLA+06 |  |  |  | 3060.8 | 290.75 | 363.2 | 218.3 | 581.5 | 174.3738 | 104.4876 | 278.8614 | 176.7061 | 105.9925 | 282.6986 | Tower PU56 to be removed | 648082.797 | 1081145.345 | 1.959 | 6 |  |  |  |  | Ok
|  |  |  | 218.3 | [12 empty] | Paddy Field
11 | PU54 | KLB+06 |  |  |  | 3279.1 | 347.4 | 218.3 | 476.5 | 694.8 | 113.8124 | 229.3643 | 343.1767 | 112.3075 | 232.2322 | 344.5398 | Tower PU53 to be removed | 647995.987 | 1081345.696 | 2.334 | 6 |  |  |  |  | Ok
|  |  |  | 476.5 | [12 empty] | Road 2nos, Building 18nos, Pond, Well, 11kV Line
12 | PU52 | KLB+06 |  |  |  | 3755.6 | 442.65 | 476.5 | 408.8 | 885.3 | 247.1357 | 231.1165 | 478.2522 | 244.2678 | 222.4934 | 466.7611 | Tower PU51 to be removed | 647806.545 | 1081782.919 | 3.894 | 6 |  |  |  |  | Ok
|  |  |  | 408.8 | [12 empty] | Building 7nos, 11kV Line, Road
13 | PU50 | KLD+06 |  |  |  | 4164.4 | 318.8 | 408.8 | 228.8 | 637.6 | 177.6835 | 200.4743 | 378.1578 | 186.3066 | 172.6927 | 358.9993 |  | 647644.025 | 1082158.004 | -0.13 | 6 |  |  |  |  | Ok
|  |  |  | 228.8 | [12 empty] | Building
14 | PU49 | KLD+00 |  |  | 1695.6 | 4393.2 | 114.4 | 228.8 | 0 | 228.8 | 28.3257 | 0 | 28.3257 | 56.1073 | 0 | 56.1073 |  | 647553.073 | 1082367.917 | -1.386 | 0 |  |  |  |  | Ok

## TSD
Sag Tension details for 220kV M/C KM TL (Wind Zone-2)
Crossarm_Ht | 13.88 | 13.88
GC | 6.25
Row | 22
T_Hot | 1794
T_Cold | 2649
Cond_Wt | 0.976
Hor_Grid | 20
Ver_Grid | 2
Hor_Scale | 1000
Ver_Scale | 100
Plot_Scale | 2000
Sheet_Gap | 220
PandP_Dist | 185
Grid_Ht | 1000