## TS
NAME OF PROJECT :- 220kV/110kV M/C MV KOTTAYAM - ETTUMANOOR TRANSMISSION LINE
NAME OF CLIENT :- KERALA STATE ELECTRICITY BOARD
NAME OF AGENCY :- FOR SOLUTIONS
DETAILED SURVEY TOWER SCHEDULE (LINE LENGTH: 6.477 Km)
Sl No | Loc No. | Tower Type | Deviation Angle (DMS) | Span (m) | Section Length (m) | Cum. Chainage (m) | Wind Span (m) | Adjacent Span |  |  | Weight Span (Cold) |  |  | Weight Span (Hot) |  |  | Major Crossings/Remarks | UTM Coordinate (Zone - 43P) |  |  | Twr Extn | Chimney Ht | Spherical Coordinate |  | Existing Tower No. | Weight Span Check | Land Use | Soil Clasification
[8 empty] | Left | Right | Total | Left | Right | Total | Left | Right | Total |  | Easting | Northing | Elevation |  |  | Longitude | Latitude
0 | Bay3 | Gantry |  |  | 0 | 0 | 226.35 | 0 | 64.7 | 64.7 | 0 | -138.4604 | -138.4604 | 0 | -83.3291 | -83.3291 | Gantry | 670651.9049 | 1071451.3932 | 27.6802 | -5.88 |  |  |  |  | Ok
64.7
1 | 229B | D60+04.5 | 94°07'14" RT |  | 64.7 | 64.7 | 48.2 | 64.7 | 31.7 | 96.4 | 203.1604 | 15.85 | 219.0104 | 148.0291 | 15.85 | 163.8791 | D60+04.5 towers to be used (Bottom Circuit) | 670598.6854 | 1071414.5978 | 24.889 | 0.983 |  |  |  |  | Ok
|  |  |  | 31.7 | [12 empty] | Compound Wall 2nos, Road, 11kV Line, Building 6nos, Well 2nos
2 | 229 | D60+04.5 | 50°45'04" RT |  | 31.7 | 96.4 | 15.85 | 31.7 | 175.1 | 206.8 | 15.85 | -3.7 | 12.15 | 15.85 | 25.7 | 41.55 | Terminal Tower | 670582.571 | 1071441.912 | 24.889 | 0.983 |  |  |  |  | Ok
0 | Bay2 | Gantry |  |  | 0 | 0 | 229.05 | 0 | 70.1 | 70.1 | 0 | -122.6024 | -122.6024 | 0 | -71.718 | -71.718 | Gantry | 670646.5428 | 1071470.6703 | 27.6802 | -5.88 |  |  |  |  | Ok
|  |  |  | 70.1 | [12 empty] | Building
2 | 229 | D60+04.5 | 134°25'06" RT |  | 70.1 | 70.1 | 122.6 | 70.1 | 175.1 | 245.2 | 192.7024 | -3.7325 | 188.9699 | 141.818 | 25.7301 | 167.5481 | D60+04.5 towers to be used (Bottom Circuit) | 670582.571 | 1071441.912 | 24.889 | 0.983 |  |  |  |  | Ok
|  |  |  | 175.1 | [12 empty] | Compound Wall 2nos, Road, 11kV Line, Building 6nos, Well 2nos
3 | 228 | KLD+03 | 11°02'35" LT |  | 175.1 | 245.2 | 176.55 | 175.1 | 178 | 353.1 | 178.8325 | 44.4912 | 223.3237 | 149.3699 | 58.857 | 208.2268 | Terminal Tower | 670643.085 | 1071606.276 | 28.761 | 3 |  |  |  |  | Ok
|  |  |  | 178 | [12 empty] | 11kV Line 2nos, Building 2nos, Well, Road
4 | 227 | KLB+00 | 02°07'48" LT |  | 178 | 423.2 | 184.4 | 178 | 190.8 | 368.8 | 133.5088 | 6.9629 | 140.4717 | 119.143 | 35.5071 | 154.6501 |  | 670671.453 | 1071782.024 | 34.68 | 0 |  |  |  |  | Ok
|  |  |  | 190.8 | [12 empty] | Well, Building, 11kV Line
5 | 226 | KLB+00 |  |  |  | 614 | 172.2 | 190.8 | 153.6 | 344.4 | 183.8371 | -333.5192 | -149.6821 | 155.2929 | -201.0832 | -45.7904 |  | 670694.838 | 1071971.413 | 40.897 | 0 |  |  |  |  | Ok
|  |  |  | 153.6 | [12 empty] | 11kV Line, Road, LT Line, Building 5nos
6 | 225 | MLD+06 | 00°00'00" |  | 344.4 | 767.6 | 189.6 | 153.6 | 225.6 | 379.2 | 487.1192 | -189.6292 | 297.49 | 354.6832 | -92.0162 | 262.667 | MLD Tower at crosing of both lines, Tower shifted by 40.5m towards 226 | 670713.658 | 1072123.826 | 53.098 | 11.02 |  |  |  |  | Ok
|  |  |  | 225.6 | [12 empty] | 11kV Line 3nos, LT Line 2nos, Well 2nos, Building 4nos
7 | 224 | KLB+03 |  |  |  | 993.2 | 174.35 | 225.6 | 123.1 | 348.7 | 415.2292 | 52.4441 | 467.6733 | 317.6162 | 55.3831 | 372.9993 |  | 670741.302 | 1072347.703 | 86.256 | 3 |  |  |  |  | Ok
|  |  |  | 123.1 | [12 empty] | 11kV Line, Building 2nos
8 | 223 | KLB+00 | 06°12'45" RT |  | 348.7 | 1116.3 | 288.85 | 123.1 | 454.6 | 577.7 | 70.6559 | 337.1552 | 407.8111 | 67.7169 | 301.698 | 369.4148 | Tower 222 to be removed | 670756.386 | 1072469.857 | 89.669 | 0 |  |  |  |  | Ok
|  |  |  | 454.6 | [12 empty] | 11kV Line 3nos, Road 2nos, Transformer, LT Line, Building
9 | 221 | KLB+03 | 00°06'32" LT |  | 454.6 | 1570.9 | 404.5 | 454.6 | 354.4 | 809 | 117.4448 | 405.2903 | 522.7351 | 152.902 | 331.6711 | 484.5732 | Tower 220 to be removed | 670860.582 | 1072912.304 | 68.269 | 3 |  |  |  |  | Ok
|  |  |  | 354.4 | [12 empty] | Building, Road, 11kV Line 3nos, LT Line, Well
10 | 219 | KLB+03 |  |  |  | 1925.3 | 289 | 354.4 | 223.6 | 578 | -50.8903 | 194.6444 | 143.754 | 22.7289 | 167.9052 | 190.6341 |  | 670941.16 | 1073257.402 | 38.486 | 3 |  |  |  |  | Ok
|  |  |  | 223.6 | [12 empty] | 11kV Line
11 | 218 | KLB+06 |  |  |  | 2148.9 | 304.95 | 223.6 | 386.3 | 609.9 | 28.9556 | 314.7347 | 343.6904 | 55.6948 | 275.4916 | 331.1864 |  | 670991.997 | 1073475.125 | 28.661 | 6 |  |  |  |  | Ok
|  |  |  | 386.3 | [12 empty] | Building 9nos, 11kV Line, Road 2nos, LT Line 3nos, Nala, Well 3nos
12 | 216 | KLA+06 |  |  |  | 2535.2 | 305.35 | 386.3 | 224.4 | 610.7 | 71.5653 | 99.3308 | 170.8961 | 110.8084 | 103.4845 | 214.2929 | Tower 217 to be removed | 671079.833 | 1073851.307 | 11.356 | 6 |  |  |  |  | Ok
|  |  |  | 224.4 | [12 empty] | Nala, 11kV Line, River, Paddy Field
13 | 215 | KLA+09 |  |  |  | 2759.6 | 314.2 | 224.4 | 404 | 628.4 | 125.0692 | 184.0222 | 309.0914 | 120.9155 | 189.8248 | 310.7402 | Tower 214 to be removed | 671130.859 | 1074069.839 | 9.42 | 9 |  |  |  |  | Ok
|  |  |  | 404 | [12 empty] | LT Line, 11kV Line, Road, Paddy Field
14 | 213 | KLC+06 | 13°32'12" LT |  | 1592.7 | 3163.6 | 368.5 | 404 | 333 | 737 | 219.9778 | 150.9161 | 370.8939 | 214.1752 | 155.946 | 370.1213 | Tower 212 to be removed | 671222.719 | 1074463.258 | 15.096 | 6 |  |  |  |  | Ok
|  |  |  | 333 | [12 empty] | 11kV Line, Road, LT Line
15 | 211 | KLA+06 | 00°21'41" LT |  | 333 | 3496.6 | 286 | 333 | 239 | 572 | 182.0839 | 135.9892 | 318.0731 | 177.054 | 130.6671 | 307.7211 |  | 671220.43 | 1074796.268 | 17.008 | 6 |  |  |  |  | Ok
|  |  |  | 239 | [12 empty] | Well 2nos, Building 5nos, 11kV Line, LT Line
16 | 210 | KLB+09 | 00°06'35" RT |  | 239 | 3735.6 | 337.05 | 239 | 435.1 | 674.1 | 103.0108 | 227.1315 | 330.1423 | 108.3329 | 224.039 | 332.3718 | Tower 209 to be removed | 671217.701 | 1075035.203 | 12.556 | 9 |  |  |  |  | Ok
|  |  |  | 435.1 | [12 empty] | LT Line 2nos, Road 2nos, 11kV Line, Paddy Field
17 | 208 | KLB+09 |  |  |  | 4170.7 | 423.8 | 435.1 | 412.5 | 847.6 | 207.9685 | 200.1177 | 408.0862 | 211.061 | 202.097 | 413.158 | Tower 207 to be removed | 671212.733 | 1075470.235 | 11.02 | 9 |  |  |  |  | Ok
|  |  |  | 412.5 | [12 empty] | Nala, Mud Road, LT Line, Paddy Field
18 | 206 | KLB+09 |  |  |  | 4583.2 | 405.55 | 412.5 | 398.6 | 811.1 | 212.3823 | 213.395 | 425.7773 | 210.403 | 208.8457 | 419.2487 |  | 671208.022 | 1075882.748 | 11.952 | 9 |  |  |  |  | Ok
|  |  |  | 398.6 | [12 empty] | Nala, Building, Mud Road, Paddy Field
19 | 204 | KLA+06 |  |  |  | 4981.8 | 316.65 | 398.6 | 234.7 | 633.3 | 185.205 | 101.7845 | 286.9895 | 189.7543 | 106.8084 | 296.5628 | Tower 205 to be removed | 671203.47 | 1076281.302 | 12.882 | 6 |  |  |  |  | Ok
|  |  |  | 234.7 | [12 empty] | Paddy Field, Building 4nos, 11kV Line, Road, Transformer
20 | 203 | KLA+06 |  |  |  | 5216.5 | 216.95 | 234.7 | 199.2 | 433.9 | 132.9155 | 179.9069 | 312.8225 | 127.8916 | 153.9868 | 281.8783 |  | 671200.79 | 1076515.977 | 14.228 | 6 |  |  |  |  | Ok
|  |  |  | 199.2 | [12 empty] | Building 2nos, Pond 2nos, Well, Paddy Field
21 | 202 | KLD+00 | 00°00'30" LT |  | 1680.1 | 5415.7 | 249.65 | 199.2 | 300.1 | 499.3 | 19.2931 | 191.1012 | 210.3943 | 45.2132 | 177.8514 | 223.0646 |  | 671198.516 | 1076715.123 | 14.334 | 0 |  |  |  |  | Ok
|  |  |  | 300.1 | [12 empty] | Nala
22 | AP1 | KLB+00 | 01°49'39" RT |  | 300.1 | 5715.8 | 266.1 | 300.1 | 232.1 | 532.2 | 108.9988 | 9.0514 | 118.0502 | 122.2486 | 43.5866 | 165.8352 |  | 671046.077 | 1076973.595 | 9.795 | 0 |  |  |  |  | Ok
|  |  |  | 232.1 | [12 empty] | Road, Nala
23 | AP2 | KLC+09 | 26°56'18" LT |  | 232.1 | 5947.9 | 279.8 | 232.1 | 327.5 | 559.6 | 223.0486 | 226.6849 | 449.7335 | 188.5134 | 206.3718 | 394.8852 |  | 670934.725 | 1077177.183 | 9.945 | 9 |  |  |  |  | Ok
|  |  |  | 327.5 | [12 empty] | Mud Road 2nos, Nala 2nos, Well, Compound Wall
24 | AP3 | KLC+00 | 26°05'22" LT |  | 327.5 | 6275.4 | 226.4 | 327.5 | 125.3 | 452.8 | 100.8151 | 64.4479 | 165.263 | 121.1282 | 63.8676 | 184.9958 |  | 670664.426 | 1077362.158 | 11.351 | 0 |  |  |  |  | Ok
|  |  |  | 125.3 | [12 empty] | Nala
25 | AP4 | KLD+00 | 90°00'00" RT |  | 125.3 | 6400.7 | 81.4 | 125.3 | 37.5 | 162.8 | 60.8521 | 18.75 | 79.6021 | 61.4324 | 18.75 | 80.1824 |  | 670540.431 | 1077380.238 | 11.268 | 0 |  |  |  |  | Ok
37.5
26 | AP5 | KLD+00 |  |  | 37.5 | 6438.2 | 18.75 | 37.5 | 0 | 37.5 | 18.75 | 0 | 18.75 | 18.75 | 0 | 18.75 |  | 670545.847 | 1077417.377 | 11.268 | 0 |  |  |  |  | Ok
0 | Bay1 | Gantry |  |  | 0 | 0 | 9.85 | 0 | 19.7 | 19.7 | 0 | 50.6861 | 50.6861 | 0 | 37.5057 | 37.5057 | Bay1 (Top Circuit) | 670732.3506 | 1071502.0978 | 27.9766 | 0 |  |  |  |  | Ok
19.7
1A | 229A | KLD+00 | 21°10'14" LT |  | 19.7 | 19.7 | 253.3 | 19.7 | 118.6 | 138.3 | -30.9861 | -34.0884 | -65.0744 | -17.8057 | -3.946 | -21.7517 | Terminal Tower | 670724.8461 | 1071520.3107 | 27.6802 | 0 |  |  |  |  | Ok
118.6
2 | 228 | KLD+03 | 52°43'60" RT |  | 118.6 | 138.3 | 148.3 | 118.6 | 178 | 296.6 | 152.6884 | 44.4912 | 197.1795 | 122.546 | 58.857 | 181.403 |  | 670643.0848 | 1071606.2761 | 28.761 | 3 |  |  |  |  | Ok
178
3 | 227 | KLB+00 | 02°07'48" LT |  | 178 | 316.3 | 89 | 178 | 0 | 178 | 133.5088 | 7 | 140.5088 | 119.143 | 35.5 | 154.643 |  | 670671.453 | 1071782.024 | 34.68 | 0 |  |  |  |  | Ok
5A | 225A | D60+00 | [14 empty] | Tower used to carry bottom circuit

## TSD
Sag Tension details for 220kV M/C KM TL (Wind Zone-2)
Crossarm_Ht | 13.88 | 13.88
GC | 6.25
Row | 22
T_Hot | 1794
T_Cold | 2649
Cond_Wt | 0.976
Hor_Grid | 20
Ver_Grid | 2
Hor_Scale | 1000
Ver_Scale | 100
Plot_Scale | 2000
Sheet_Gap | 220
PandP_Dist | 185
Grid_Ht | 1000